## model_setup
wildcard | existing_eskom_stations | existing_non_eskom_stations | new_build | projected_parameters | costs
za-original | base | original | original | base | original
za-updated | base | base | base | base | original
IRP-2019 | base | base | base | base | irp_2019
CSIR-2019 | base | base | base | base | csir_2019

## existing_eskom_stations
Scenario | Power Station Name | Carrier | Status | 2022 Capacity (MW) | Unit size (MW) | Number units | Future Commissioning Date | Decommissioning Date (50%) | Decommissioning Date (100%) | Heat Rate (GJ/MWh) | Fuel Price (R/GJ) | Max Ramp Up (MW/min) | Max Ramp Down (MW/min) | Min Stable Level (%) | Variable O&M Cost (R/MWh) | Fixed O&M Cost (R/kW/yr) | Pump Efficiency (%) | Pump Units | Pump Load per unit (MW) | Pumped Storage - Max Storage (GWh) | CSP Storage (hours) | Diesel Storage (Ml) | Gas storage (MCM) | Typical annual maintenance rate (%) | Typical annual forced outage rate (%) | GPS Latitude | GPS Longitude
original | Arnot | coal | Existing | 2100 | 370 | 6 | - | - | 2025-01-01 | 11.654 | 16.8 | 2.1 | 2.1 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -25.9444 | 29.7917
original | Camden | coal | Existing | 1481 | 190 | 8 | - | - | 2023-01-01 | 12.421 | 23.1 | 1.1 | 1.1 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.6201 | 30.0911
original | Duvha | coal | Existing | 2875 | 580 | 5 | - | - | 2034-01-01 | 11.034 | 11.8 | 3.3 | 3.3 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -25.9595 | 29.3409
original | Grootvlei | coal | Existing | 570 | 180 | 6 | - | - | 2028-01-01 | 12.61 | 22.1 | 0.9 | 0.9 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.7695 | 28.4995
original | Hendrina | coal | Existing | 1098 | 190 | 10 | - | - | 2026-01-01 | 12.131 | 17 | 1.1 | 1.1 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.0314 | 29.6014
original | Kendal | coal | Existing | 3840 | 640 | 6 | - | - | 2043-01-01 | 11.753 | 18.6 | 1.8 | 1.8 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.088 | 28.9689
original | Komati | coal | Existing | 114 | 100 | 9 | - | - | 2028-01-01 | 13.829 | 17.6 | 0.5 | 0.5 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.0908 | 29.4745
original | Kriel | coal | Existing | 2850 | 480 | 6 | - | - | 2029-01-01 | 11.243 | 18.6 | 3.6 | 3.6 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.254 | 29.1801
original | Kusile | coal | Existing | 2880 | 723 | 0 | - | - | beyond 2050 | 9.812 | 16.3 | 7.2 | 7.2 | 30% | 80 | 4700 | - | - | - | - | - |  |  | 10% | 10% | -25.5459 | 28.5502
original | Lethabo | coal | Existing | 3558 | 590 | 6 | - | - | 2040-01-01 | 10.975 | 11.2 | 5.9 | 5.9 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.7403 | 27.975
original | MajubaDry | coal | Existing | 1833 | 610 | 3 | - | - | 2048-01-01 | 11.753 | 21.8 | 1.7 | 1.7 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -27.0955 | 29.7706
original | MajubaWet | coal | Existing | 2010 | 670 | 3 | - | - | 2051-01-01 | 11.004 | 23.3 | 1.9 | 1.9 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -27.0955 | 29.7706
original | Matimba | coal | Existing | 3690 | 620 | 6 | - | - | 2041-01-01 | 11.654 | 11.4 | 3 | 3 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -23.6678 | 27.6128
original | Matla | coal | Existing | 3450 | 580 | 6 | - | - | 2033-01-01 | 11.034 | 22.9 | 2.4 | 2.4 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.2804 | 29.1423
original | Medupi | coal | Existing | 3597 | 722 | 1 | - | - | beyond 2050 | 9.812 | 16.3 | 7.2 | 7.2 | 30% | 80 | 4700 | - | - | - | - | - |  |  | 10% | 10% | -23.42 | 27.33
original | Tutuka | coal | Existing | 3510 | 580 | 6 | - | - | 2040-01-01 | 10.918 | 26 | 3.2 | 3.2 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.7756 | 29.3521
original | Sere | onwind | Existing | 100 | 2 | 50 | - | - | 2034-04-30 | - | - | - | - | 0% | 700 | 0 | - | - | - | - | - |  |  | 10% | 10% | -31.5018 | 18.1143
original | Koeberg | nuclear | Existing | 1854 | 930 | 2 | - | - | 2044-01-01 | 11.111 | 8.1 | - | - | 40% | 37 | 968 | - | - | - | - | - |  |  | 3% | 6% | -33.6737 | 18.4281
original | Drakensberg | PHS | Existing | 1000 | 250 | 4 | - | - | beyond 2050 | - | - | - | - | 0% | 0 | 201 | 73.7% | 4 | 250 | 21.7 | - |  |  | 3% | 2.4% | -28.5628 | 29.0828
original | Ingula | PHS | Existing | 1332 | 333 | 4 | - | - | beyond 2050 | - | - | - | - | 0% | 0 | 2530 | 78% | 4 | 333 | 27.4 | - |  |  | 3% | 2.4% | -28.165 | 29.3512
original | Palmiet | PHS | Existing | 400 | 200 | 2 | - | - | beyond 2050 | - | - | - | - | 0% | 0 | 201 | 77.9% | 2 | 200 | 10 | - |  |  | 3% | 2.4% | -34.1972 | 18.9736
original | Gariep | hydro | Existing | 360 | 90 | 4 | - | - | beyond 2050 | - | - | - | - | 0% | 30 | 0 | - | - | - | - | - |  |  | 3% | 2.4% | -30.624 | 25.504
original | Vanderkloof | hydro | Existing | 240 | 120 | 2 | - | - | beyond 2050 | - | - | - | - | 0% | 30 | 0 | - | - | - | - | - |  |  | 3% | 2.4% | -29.9934 | 24.7338
original | Acacia | diesel | Existing | 171 | 57 | 3 | - | - | 2025-12-31 | 11.519 | 270 | 3.4 | 3.4 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -33.8841 | 18.5336
original | Ankerlig | diesel | Existing | 1327 | 148 | 9 | - | - | 2036-12-31 | 11.519 | 250 | 9 | 9 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -33.592 | 18.4607
original | Gourikwa | diesel | Existing | 740 | 148 | 5 | - | - | 2036-12-31 | 11.519 | 250 | 9 | 9 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -34.1653 | 21.9608
original | PortRex | diesel | Existing | 171 | 57 | 3 | - | - | 2025-12-31 | 11.519 | 270 | 3.4 | 3.4 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -33.0274 | 27.8838
base | Arnot | coal | Existing | 2100 | 370 | 6 | - | - | 2025-01-01 | 11.654 | 16.8 | 2.1 | 2.1 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -25.9444 | 29.7917
base | Camden | coal | Existing | 1481 | 190 | 8 | - | - | 2023-01-01 | 12.421 | 23.1 | 1.1 | 1.1 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.6201 | 30.0911
base | Duvha | coal | Existing | 2875 | 580 | 5 | - | - | 2034-01-01 | 11.034 | 11.8 | 3.3 | 3.3 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -25.9595 | 29.3409
base | Grootvlei | coal | Existing | 570 | 180 | 6 | - | - | 2028-01-01 | 12.61 | 22.1 | 0.9 | 0.9 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.7695 | 28.4995
base | Hendrina | coal | Existing | 1098 | 190 | 10 | - | - | 2026-01-01 | 12.131 | 17 | 1.1 | 1.1 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.0314 | 29.6014
base | Kendal | coal | Existing | 3840 | 640 | 6 | - | - | 2043-01-01 | 11.753 | 18.6 | 1.8 | 1.8 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.088 | 28.9689
base | Komati | coal | Existing | 114 | 100 | 9 | - | - | 2028-01-01 | 13.829 | 17.6 | 0.5 | 0.5 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.0908 | 29.4745
base | Kriel | coal | Existing | 2850 | 480 | 6 | - | - | 2029-01-01 | 11.243 | 18.6 | 3.6 | 3.6 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.254 | 29.1801
base | Kusile | coal | Existing | 2880 | 723 | 0 | - | - | beyond 2050 | 9.812 | 16.3 | 7.2 | 7.2 | 30% | 80 | 4700 | - | - | - | - | - |  |  | 10% | 10% | -25.5459 | 28.5502
base | Lethabo | coal | Existing | 3558 | 590 | 6 | - | - | 2040-01-01 | 10.975 | 11.2 | 5.9 | 5.9 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.7403 | 27.975
base | MajubaDry | coal | Existing | 1833 | 610 | 3 | - | - | 2048-01-01 | 11.753 | 21.8 | 1.7 | 1.7 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -27.0955 | 29.7706
base | MajubaWet | coal | Existing | 2010 | 670 | 3 | - | - | 2051-01-01 | 11.004 | 23.3 | 1.9 | 1.9 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -27.0955 | 29.7706
base | Matimba | coal | Existing | 3690 | 620 | 6 | - | - | 2041-01-01 | 11.654 | 11.4 | 3 | 3 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -23.6678 | 27.6128
base | Matla | coal | Existing | 3450 | 580 | 6 | - | - | 2033-01-01 | 11.034 | 22.9 | 2.4 | 2.4 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.2804 | 29.1423
base | Medupi | coal | Existing | 3597 | 722 | 1 | - | - | beyond 2050 | 9.812 | 16.3 | 7.2 | 7.2 | 30% | 80 | 4700 | - | - | - | - | - |  |  | 10% | 10% | -23.42 | 27.33
base | Tutuka | coal | Existing | 3510 | 580 | 6 | - | - | 2040-01-01 | 10.918 | 26 | 3.2 | 3.2 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.7756 | 29.3521
base | Sere | onwind | Existing | 100 | 2 | 50 | - | - | 2034-04-30 | - | - | - | - | 0% | 700 | 0 | - | - | - | - | - |  |  | 10% | 10% | -31.5018 | 18.1143
base | Koeberg | nuclear | Existing | 1854 | 930 | 2 | - | - | 2044-01-01 | 11.111 | 8.1 | - | - | 40% | 37 | 968 | - | - | - | - | - |  |  | 3% | 6% | -33.6737 | 18.4281
base | Drakensberg | PHS | Existing | 1000 | 250 | 4 | - | - | beyond 2050 | - | - | - | - | 0% | 0 | 201 | 73.7% | 4 | 250 | 21.7 | - |  |  | 3% | 2.4% | -28.5628 | 29.0828
base | Ingula | PHS | Existing | 1332 | 333 | 4 | - | - | beyond 2050 | - | - | - | - | 0% | 0 | 2530 | 78% | 4 | 333 | 27.4 | - |  |  | 3% | 2.4% | -28.165 | 29.3512
base | Palmiet | PHS | Existing | 400 | 200 | 2 | - | - | beyond 2050 | - | - | - | - | 0% | 0 | 201 | 77.9% | 2 | 200 | 10 | - |  |  | 3% | 2.4% | -34.1972 | 18.9736
base | Gariep | hydro | Existing | 360 | 90 | 4 | - | - | beyond 2050 | - | - | - | - | 0% | 30 | 0 | - | - | - | - | - |  |  | 3% | 2.4% | -30.624 | 25.504
base | Vanderkloof | hydro | Existing | 240 | 120 | 2 | - | - | beyond 2050 | - | - | - | - | 0% | 30 | 0 | - | - | - | - | - |  |  | 3% | 2.4% | -29.9934 | 24.7338
base | Acacia | diesel | Existing | 0 | 57 | 3 | - | - | 2025-12-31 | 11.519 | 270 | 3.4 | 3.4 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -33.8841 | 18.5336
base | Ankerlig | diesel | Existing | 1327 | 148 | 9 | - | - | 2036-12-31 | 11.519 | 250 | 9 | 9 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -33.592 | 18.4607
base | Gourikwa | diesel | Existing | 740 | 148 | 5 | - | - | 2036-12-31 | 11.519 | 250 | 9 | 9 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -34.1653 | 21.9608
base | PortRex | diesel | Existing | 0 | 57 | 3 | - | - | 2025-12-31 | 11.519 | 270 | 3.4 | 3.4 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -33.0274 | 27.8838
ambitions | Arnot | coal | Existing | 2100 | 370 | 6 | - | 2024-01-01 | 2025-01-01 | 11.654 | 16.8 | 2.1 | 2.1 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -25.9444 | 29.7917
ambitions | Camden | coal | Existing | 1481 | 190 | 8 | - | 2022-01-01 | 2023-01-01 | 12.421 | 23.1 | 1.1 | 1.1 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.6201 | 30.0911
ambitions | Duvha | coal | Existing | 2875 | 580 | 5 | - | 2033-01-01 | 2034-01-01 | 11.034 | 11.8 | 3.3 | 3.3 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -25.9595 | 29.3409
ambitions | Grootvlei | coal | Existing | 570 | 180 | 6 | - | 2027-01-01 | 2028-01-01 | 12.61 | 22.1 | 0.9 | 0.9 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.7695 | 28.4995
ambitions | Hendrina | coal | Existing | 1098 | 190 | 10 | - | 2025-01-01 | 2026-01-01 | 12.131 | 17 | 1.1 | 1.1 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.0314 | 29.6014
ambitions | Kendal | coal | Existing | 3840 | 640 | 6 | - | 2042-01-01 | 2043-01-01 | 11.753 | 18.6 | 1.8 | 1.8 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.088 | 28.9689
ambitions | Komati | coal | Existing | 114 | 100 | 9 | - | 2027-01-01 | 2028-01-01 | 13.829 | 17.6 | 0.5 | 0.5 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.0908 | 29.4745
ambitions | Kriel | coal | Existing | 2850 | 480 | 6 | - | 2028-01-01 | 2029-01-01 | 11.243 | 18.6 | 3.6 | 3.6 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.254 | 29.1801
ambitions | Kusile | coal | Existing | 2880 | 723 | 0 | - | - | beyond 2050 | 9.812 | 16.3 | 7.2 | 7.2 | 30% | 80 | 4700 | - | - | - | - | - |  |  | 10% | 10% | -25.5459 | 28.5502
ambitions | Lethabo | coal | Existing | 3558 | 590 | 6 | - | 2039-01-01 | 2040-01-01 | 10.975 | 11.2 | 5.9 | 5.9 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.7403 | 27.975
ambitions | MajubaDry | coal | Existing | 1833 | 610 | 3 | - | 2047-01-01 | 2048-01-01 | 11.753 | 21.8 | 1.7 | 1.7 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -27.0955 | 29.7706
ambitions | MajubaWet | coal | Existing | 2010 | 670 | 3 | - | 2050-01-01 | 2051-01-01 | 11.004 | 23.3 | 1.9 | 1.9 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -27.0955 | 29.7706
ambitions | Matimba | coal | Existing | 3690 | 620 | 6 | - | 2040-01-01 | 2041-01-01 | 11.654 | 11.4 | 3 | 3 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -23.6678 | 27.6128
ambitions | Matla | coal | Existing | 3450 | 580 | 6 | - | 2032-01-01 | 2033-01-01 | 11.034 | 22.9 | 2.4 | 2.4 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.2804 | 29.1423
ambitions | Medupi | coal | Existing | 3597 | 722 | 1 | - | - | beyond 2050 | 9.812 | 16.3 | 7.2 | 7.2 | 30% | 80 | 4700 | - | - | - | - | - |  |  | 10% | 10% | -23.42 | 27.33
ambitions | Tutuka | coal | Existing | 3510 | 580 | 6 | - | 2039-01-01 | 2040-01-01 | 10.918 | 26 | 3.2 | 3.2 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.7756 | 29.3521
ambitions | Sere | onwind | Existing | 100 | 2 | 50 | - | 2033-04-30 | 2034-04-30 | - | - | - | - | 0% | 700 | 0 | - | - | - | - | - |  |  | 10% | 10% | -31.5018 | 18.1143
ambitions | Koeberg | nuclear | Existing | 1854 | 930 | 2 | - | 2043-01-01 | 2044-01-01 | 11.111 | 8.1 | - | - | 40% | 37 | 968 | - | - | - | - | - |  |  | 3% | 6% | -33.6737 | 18.4281
ambitions | Drakensberg | PHS | Existing | 1000 | 250 | 4 | - | - | beyond 2050 | - | - | - | - | 0% | 0 | 201 | 73.7% | 4 | 250 | 21.7 | - |  |  | 3% | 2.4% | -28.5628 | 29.0828
ambitions | Ingula | PHS | Existing | 1332 | 333 | 4 | - | - | beyond 2050 | - | - | - | - | 0% | 0 | 2530 | 78% | 4 | 333 | 27.4 | - |  |  | 3% | 2.4% | -28.165 | 29.3512
ambitions | Palmiet | PHS | Existing | 400 | 200 | 2 | - | - | beyond 2050 | - | - | - | - | 0% | 0 | 201 | 77.9% | 2 | 200 | 10 | - |  |  | 3% | 2.4% | -34.1972 | 18.9736
ambitions | Gariep | hydro | Existing | 360 | 90 | 4 | - | - | beyond 2050 | - | - | - | - | 0% | 30 | 0 | - | - | - | - | - |  |  | 3% | 2.4% | -30.624 | 25.504
ambitions | Vanderkloof | hydro | Existing | 240 | 120 | 2 | - | - | beyond 2050 | - | - | - | - | 0% | 30 | 0 | - | - | - | - | - |  |  | 3% | 2.4% | -29.9934 | 24.7338
ambitions | Acacia | OCGT/ICE | Existing | 171 | 57 | 3 | - | 2024-12-31 | 2025-12-31 | 11.519 | 270 | 3.4 | 3.4 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -33.8841 | 18.5336
ambitions | Ankerlig | OCGT/ICE | Existing | 1327 | 148 | 9 | - | 2035-12-31 | 2036-12-31 | 11.519 | 250 | 9 | 9 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -33.592 | 18.4607
ambitions | Gourikwa | OCGT/ICE | Existing | 740 | 148 | 5 | - | 2035-12-31 | 2036-12-31 | 11.519 | 250 | 9 | 9 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -34.1653 | 21.9608
ambitions | PortRex | OCGT/ICE | Existing | 171 | 57 | 3 | - | 2024-12-31 | 2025-12-31 | 11.519 | 270 | 3.4 | 3.4 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -33.0274 | 27.8838
ambitions_2Gt | Arnot | coal | Existing | 2100 | 370 | 6 | - | 2024-01-01 | 2025-01-01 | 11.654 | 16.8 | 2.1 | 2.1 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -25.9444 | 29.7917
ambitions_2Gt | Camden | coal | Existing | 1481 | 190 | 8 | - | 2022-01-01 | 2023-01-01 | 12.421 | 23.1 | 1.1 | 1.1 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.6201 | 30.0911
ambitions_2Gt | Duvha | coal | Existing | 2875 | 580 | 5 | - | 2033-01-01 | 2034-01-01 | 11.034 | 11.8 | 3.3 | 3.3 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -25.9595 | 29.3409
ambitions_2Gt | Grootvlei | coal | Existing | 570 | 180 | 6 | - | 2027-01-01 | 2028-01-01 | 12.61 | 22.1 | 0.9 | 0.9 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.7695 | 28.4995
ambitions_2Gt | Hendrina | coal | Existing | 1098 | 190 | 10 | - | 2025-01-01 | 2026-01-01 | 12.131 | 17 | 1.1 | 1.1 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.0314 | 29.6014
ambitions_2Gt | Kendal | coal | Existing | 3840 | 640 | 6 | - | 2042-01-01 | 2043-01-01 | 11.753 | 18.6 | 1.8 | 1.8 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.088 | 28.9689
ambitions_2Gt | Komati | coal | Existing | 114 | 100 | 9 | - | 2027-01-01 | 2028-01-01 | 13.829 | 17.6 | 0.5 | 0.5 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.0908 | 29.4745
ambitions_2Gt | Kriel | coal | Existing | 2850 | 480 | 6 | - | 2028-01-01 | 2029-01-01 | 11.243 | 18.6 | 3.6 | 3.6 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.254 | 29.1801
ambitions_2Gt | Kusile | coal | Existing | 2880 | 723 | 0 | - | - | beyond 2050 | 9.812 | 16.3 | 7.2 | 7.2 | 30% | 80 | 4700 | - | - | - | - | - |  |  | 10% | 10% | -25.5459 | 28.5502
ambitions_2Gt | Lethabo | coal | Existing | 3558 | 590 | 6 | - | 2039-01-01 | 2040-01-01 | 10.975 | 11.2 | 5.9 | 5.9 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.7403 | 27.975
ambitions_2Gt | MajubaDry | coal | Existing | 1833 | 610 | 3 | - | 2047-01-01 | 2048-01-01 | 11.753 | 21.8 | 1.7 | 1.7 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -27.0955 | 29.7706
ambitions_2Gt | MajubaWet | coal | Existing | 2010 | 670 | 3 | - | 2050-01-01 | 2051-01-01 | 11.004 | 23.3 | 1.9 | 1.9 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -27.0955 | 29.7706
ambitions_2Gt | Matimba | coal | Existing | 3690 | 620 | 6 | - | 2040-01-01 | 2041-01-01 | 11.654 | 11.4 | 3 | 3 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -23.6678 | 27.6128
ambitions_2Gt | Matla | coal | Existing | 3450 | 580 | 6 | - | 2032-01-01 | 2033-01-01 | 11.034 | 22.9 | 2.4 | 2.4 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.2804 | 29.1423
ambitions_2Gt | Medupi | coal | Existing | 3597 | 722 | 1 | - | - | beyond 2050 | 9.812 | 16.3 | 7.2 | 7.2 | 30% | 80 | 4700 | - | - | - | - | - |  |  | 10% | 10% | -23.42 | 27.33
ambitions_2Gt | Tutuka | coal | Existing | 3510 | 580 | 6 | - | 2039-01-01 | 2040-01-01 | 10.918 | 26 | 3.2 | 3.2 | 30% | 57 | 594 | - | - | - | - | - |  |  | 10% | 10% | -26.7756 | 29.3521
ambitions_2Gt | Sere | onwind | Existing | 100 | 2 | 50 | - | 2033-04-30 | 2034-04-30 | - | - | - | - | 0% | 700 | 0 | - | - | - | - | - |  |  | 10% | 10% | -31.5018 | 18.1143
ambitions_2Gt | Koeberg | nuclear | Existing | 1854 | 930 | 2 | - | 2043-01-01 | 2044-01-01 | 11.111 | 8.1 | - | - | 40% | 37 | 968 | - | - | - | - | - |  |  | 3% | 6% | -33.6737 | 18.4281
ambitions_2Gt | Drakensberg | PHS | Existing | 1000 | 250 | 4 | - | - | beyond 2050 | - | - | - | - | 0% | 0 | 201 | 73.7% | 4 | 250 | 21.7 | - |  |  | 3% | 2.4% | -28.5628 | 29.0828
ambitions_2Gt | Ingula | PHS | Existing | 1332 | 333 | 4 | - | - | beyond 2050 | - | - | - | - | 0% | 0 | 2530 | 78% | 4 | 333 | 27.4 | - |  |  | 3% | 2.4% | -28.165 | 29.3512
ambitions_2Gt | Palmiet | PHS | Existing | 400 | 200 | 2 | - | - | beyond 2050 | - | - | - | - | 0% | 0 | 201 | 77.9% | 2 | 200 | 10 | - |  |  | 3% | 2.4% | -34.1972 | 18.9736
ambitions_2Gt | Gariep | hydro | Existing | 360 | 90 | 4 | - | - | beyond 2050 | - | - | - | - | 0% | 30 | 0 | - | - | - | - | - |  |  | 3% | 2.4% | -30.624 | 25.504
ambitions_2Gt | Vanderkloof | hydro | Existing | 240 | 120 | 2 | - | - | beyond 2050 | - | - | - | - | 0% | 30 | 0 | - | - | - | - | - |  |  | 3% | 2.4% | -29.9934 | 24.7338
ambitions_2Gt | Acacia | OCGT/ICE | Existing | 171 | 57 | 3 | - | 2024-12-31 | 2025-12-31 | 11.519 | 270 | 3.4 | 3.4 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -33.8841 | 18.5336
ambitions_2Gt | Ankerlig | OCGT/ICE | Existing | 1327 | 148 | 9 | - | 2035-12-31 | 2036-12-31 | 11.519 | 250 | 9 | 9 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -33.592 | 18.4607
ambitions_2Gt | Gourikwa | OCGT/ICE | Existing | 740 | 148 | 5 | - | 2035-12-31 | 2036-12-31 | 11.519 | 250 | 9 | 9 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -34.1653 | 21.9608
ambitions_2Gt | PortRex | OCGT/ICE | Existing | 171 | 57 | 3 | - | 2024-12-31 | 2025-12-31 | 11.519 | 270 | 3.4 | 3.4 | 0% | 2 | 161 | - | - | - | - | - |  |  | 6.9% | 4.6% | -33.0274 | 27.8838
Formulas:
Decommissioning Date (50%) = DATE(YEAR([Decommissioning Date (100%)])-1,MONTH([Decommissioning Date (100%)]),DAY([Decommissioning Date (100%)]))

## existing_non_eskom_stations
| Power Station Name | Grouping | Carrier | Status | 2022 Capacity (MW) | Unit size (MW) | Number units | Future Commissioning Date | Decommissioning Date (50%) | Decommissioning Date (100%) | Heat Rate (GJ/MWh) | Fuel Price (R/GJ) | Max Ramp Up (MW/min) | Max Ramp Down (MW/min) | Min Stable Level (%) | Variable O&M Cost (R/MWh) | Fixed O&M Cost (R/kW/yr) | Pump Efficiency (%) | Pump Units | Pump Load per unit (MW) | Pumped Storage - Max Storage (GWh) | CSP Storage (hours) | Typical annual maintenance rate (%) | Typical annual forced outage rate (%) | GPS Latitude | GPS Longitude
original | Municipal_Coal | other | coal | Existing | 160 | - | - | - |  | beyond 2050 | 12.372 | 13.7 | 0.5 | 0.5 | 30% | 80 | 0 | - | - | - | - | - | 10% | 15% | -26.658 | 28.1138
original | Sasol_SSF | other | coal | Existing | 600 | - | - | - |  | beyond 2050 | 12.372 | 13.7 | 0.5 | 0.5 | 30% | 900 | 0 | - | - | - | - | - | 10% | 10% | -26.5036 | 29.1803
original | Avon | other | diesel | Existing | 670 | 167.5 | 4 | - |  | beyond 2050 | 11.519 | 250 | 11 | 11 | 0% | 2 | 101 | - | - | - | - | - | 6.9% | 4.6% | -29.251 | 31.0941
original | Dedisa | other | diesel | Existing | 335 | 167.5 | 2 | - |  | beyond 2050 | 11.519 | 250 | 11 | 11 | 0% | 2 | 101 | - | - | - | - | - | 6.9% | 4.6% | -33.4433 | 25.4022
original | Sasol_Infrach_Engines | other | gas | Existing | 175 | 9.7 | 18 | - |  | beyond 2050 | 7.6 | 200 | 8 | 8 | 0% | 950 | 0 | - | - | - | - | - | 6.9% | 4.6% | -26.8102 | 27.8277
original | Sasol_OCGT | other | gas | Existing | 250 | 50 | 5 | - |  | beyond 2050 | 11.519 | 200 | 2 | 2 | 0% | 950 | 0 | - | - | - | - | - | 6.9% | 4.6% | -26.8102 | 27.8277
original | CahoraBassa | other | hydro | Existing | 1764 | 250 | 6 | - |  | beyond 2050 | - | - | - | - | 0% | 300 | 0 | - | - | - | - | - | 3% | 3%
original | ColleyWobbles | other | hydro | Existing | 65 | 65 | 1 | - |  | beyond 2050 | - | - | - | - | 0% | 300 | 0 | - | - | - | - | - | 5% | 5% | -32.05 | 28.5833
original | Mondi | other | biomass | Existing | 120 | 30 | 4 | - |  | beyond 2050 | - | - | 0.5 | 0.5 | 0% | 500 | 0 | - | - | - | - | - | 10% | 10%
original | Sappi | other | biomass | Existing | 144 | 36 | 4 | - |  | beyond 2050 | - | - | 0.5 | 0.5 | 0% | 500 | 0 | - | - | - | - | - | 10% | 10% | -25.3447 | 30.394
original | Steenbras | other | PHS | Existing | 180 | 45 | 4 | - |  | beyond 2050 | - | - | - | - | 0% | 300 | 0 | 72% | 4 | 45 | 2.7 | - | 3% | 2.4% | -34.153 | 18.9
base | Aries Solar Energy Facility | REIPPPP_BW1 | solar | Existing | 9.65 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -29.3501 | 21.154
base | Cookhouse Wind Farm | REIPPPP_BW1 | onwind | Existing | 135.8 | - | - | - | - | 2034-01-01 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | 6% | 0% | -32.7461 | 25.807
base | Dassieklip Wind Energy Facility | REIPPPP_BW1 | onwind | Existing | 27 | - | - | - | - | 2034-01-01 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | 6% | 0% | -34.2324 | 19.4288
base | De Aar Solar Power | REIPPPP_BW1 | solar | Existing | 45.6 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -30.6599 | 24.0198
base | Dorper Wind Farm | REIPPPP_BW1 | onwind | Existing | 97.53 | - | - | - | - | 2034-01-01 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | 6% | 0% | -31.3963 | 26.3538
base | Greefspan PV Power Plant | REIPPPP_BW1 | solar | Existing | 9.9 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -29.1151 | 23.7491
base | Herbert PV Power Plant | REIPPPP_BW1 | solar | Existing | 19.9 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -29.1151 | 23.7491
base | Jeffreys Bay Wind Farm | REIPPPP_BW1 | onwind | Existing | 135.11 | - | - | - | - | 2034-01-01 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | 6% | 0% | -34.0505 | 24.9061
base | Kalkbult | REIPPPP_BW1 | solar | Existing | 72.4 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -30.4379 | 24.4704
base | Kaxu Solar One | REIPPPP_BW1 | CSP | Existing | 100 | - | - | - | - | 2045-01-01 | - | - | - | - | 0% | 3554 | 0 | - | - | - | - | 3 | 8% | 0% | -28.5252 | 19.3535
base | Khi Solar One | REIPPPP_BW1 | CSP | Existing | 50 |  |  | - | - | 2045-01-01 | - | - | - | - | 0% | 3554 | 0 | - | - | - | - | 6 | 8% | 0% | -28.3214 | 21.439
base | Konkoonsies Solar Energy Facility | REIPPPP_BW1 | solar | Existing | 9.65 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -29.1621 | 19.3863
base | Kouga Wind Farm | REIPPPP_BW1 | onwind | Existing | 77.7 | - | - | - | - | 2034-01-01 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | 6% | 0% | -34.0016 | 24.7416
base | Lesedi Power Company | REIPPPP_BW1 | solar | Existing | 64 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -28.3095 | 23.1041
base | Letsatsi Power Company | REIPPPP_BW1 | solar | Existing | 64 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -29.1121 | 26.2157
base | Metrowind Van Stadens Wind Farm | REIPPPP_BW1 | onwind | Existing | 27 | - | - | - | - | 2034-01-01 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | 6% | 0% | -33.8048 | 25.4905
base | Mulilo Renewable Energy Solar PV De Aar | REIPPPP_BW1 | solar | Existing | 10 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -30.6599 | 24.0198
base | Mulilo Renewable Energy Solar PV Prieska | REIPPPP_BW1 | solar | Existing | 19.12 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -29.9647 | 22.3394
base | Nobelsfontein Phase 1 | REIPPPP_BW1 | onwind | Existing | 73.8 | - | - | - | - | 2034-01-01 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | 6% | 0% | -31.4222 | 23.1149
base | REISA | REIPPPP_BW1 | solar | Existing | 75 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -27.7581 | 23.0159
base | RustMo1 Solar Farm | REIPPPP_BW1 | solar | Existing | 6.93 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -25.6533 | 27.2498
base | Droogfontein Solar Power | REIPPPP_BW1 | solar | Existing | 45.4 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -28.7251 | 24.7517
base | Slimsun Swartland Solar Park | REIPPPP_BW1 | solar | Existing | 5 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -33.4578 | 18.7233
base | Solar Capital De Aar | REIPPPP_BW1 | solar | Existing | 75 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -30.6599 | 24.0198
base | Soutpan Solar Park | REIPPPP_BW1 | solar | Existing | 27.94 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -23.3694 | 29.3218
base | Touwsrivier Project | REIPPPP_BW1 | solar | Existing | 36 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -33.3394 | 20.0293
base | Umoya Energy Wind Farm | REIPPPP_BW1 | onwind | Existing | 65.4 | - | - | - | - | 2034-01-01 | - | - | - | - | 0% | 1513 | 0 | - | - | - | - | - | 6% | 0% | -33.0286 | 18.3075
base | Witkop Solar Park | REIPPPP_BW1 | solar | Existing | 29.68 | - | - | - | - | 2039-01-01 | - | - | - | - | 0% | 3649 | 0 | - | - | - | - | - | 5% | 0% | -23.9023 | 29.4508
base | Amakhala Emoyeni | REIPPPP_BW2 | onwind | Existing | 131.05 | - | - | - | - | 2037-01-01 | - | - | - | - | 0% | 1186 | 0 | - | - | - | - | - | 6% | 0% | -32.6878 | 26.1064
base | Aurora Wind Power | REIPPPP_BW2 | onwind | Existing | 90.82 | - | - | - | - | 2037-01-01 | - | - | - | - | 0% | 1186 | 0 | - | - | - | - | - | 6% | 0% | -32.9079 | 17.9958
base | Aurora-Rietvlei Solar Power | REIPPPP_BW2 | solar | Existing | 8.9 | - | - | - | - | 2042-01-01 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | 5% | 0% | -32.7096 | 18.4854
base | Bokpoort CSP project | REIPPPP_BW2 | CSP | Existing | 50 | - | - | - | - | 2048-01-01 | - | - | - | - | 0% | 3324 | 0 | - | - | - | - | 9 | 8% | 0% | -28.8779 | 21.92
base | Boshoff Solar Park | REIPPPP_BW2 | solar | Existing | 57 | - | - | - | - | 2042-01-01 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | 5% | 0% | -28.5392 | 25.2131
base | Chaba Wind Farm | REIPPPP_BW2 | onwind | Existing | 21 | - | - | - | - | 2036-01-01 | - | - | - | - | 0% | 1186 | 0 | - | - | - | - | - | 6% | 0% | -32.5879 | 27.8792
base | Dreunberg | REIPPPP_BW2 | solar | Existing | 69.6 | - | - | - | - | 2042-01-01 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | 5% | 0% | -30.9974 | 26.3302
base | Gouda Wind Project | REIPPPP_BW2 | onwind | Existing | 135.5 | - | - | - | - | 2037-01-01 | - | - | - | - | 0% | 1186 | 0 | - | - | - | - | - | 6% | 0% | -33.2944 | 19.044
base | Grassridge Wind Farm | REIPPPP_BW2 | onwind | Existing | 59.8 | - | - | - | - | 2037-01-01 | - | - | - | - | 0% | 1186 | 0 | - | - | - | - | - | 6% | 0% | -33.7957 | 25.6722
base | Jasper Power Company | REIPPPP_BW2 | solar | Existing | 75 | - | - | - | - | 2042-01-01 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | 5% | 0% | -28.3095 | 23.1041
base | Linde | REIPPPP_BW2 | solar | Existing | 36.8 | - | - | - | - | 2042-01-01 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | 5% | 0% | -31.0452 | 24.4418
base | Neusberg Hydro Electrical Project | REIPPPP_BW2 | hydro | Existing | 10 | - | - | - | - | beyond 2050 | - | - | - | - | 0% | 1363 | 0 | - | - | - | - | - | 3% | 3% | -28.7527 | 20.5335
base | Sishen Solar Facility | REIPPPP_BW2 | solar | Existing | 74 | - | - | - | - | 2042-01-01 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | 5% | 0% | -27.7581 | 23.0159
base | Solar Capital De Aar 3 | REIPPPP_BW2 | solar | Existing | 75 | - | - | - | - | 2042-01-01 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | 5% | 0% | -30.6599 | 24.0198
base | Stortemelk Hydro | REIPPPP_BW2 | hydro | Existing | 4.22 | - | - | - | - | beyond 2050 | - | - | - | - | 0% | 1363 | 0 | - | - | - | - | - | 3% | 3% | -28.5142 | 28.4101
base | Tsitsikamma Community Wind Farm | REIPPPP_BW2 | onwind | Existing | 93.68 | - | - | - | - | 2037-01-01 | - | - | - | - | 0% | 1186 | 0 | - | - | - | - | - | 6% | 0% | -34.0151 | 24.3446
base | Upington Airport | REIPPPP_BW2 | solar | Existing | 8.9 | - | - | - | - | 2042-01-01 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | 5% | 0% | -28.4149 | 21.2219
base | Vredendal Solar Park | REIPPPP_BW2 | solar | Existing | 8.8 | - | - | - | - | 2042-01-01 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | 5% | 0% | -31.6556 | 18.5161
base | Waainek Wind Farm | REIPPPP_BW2 | onwind | Existing | 23.28 | - | - | - | - | 2037-01-01 | - | - | - | - | 0% | 1186 | 0 | - | - | - | - | - | 6% | 0% | -33.309 | 26.5317
base | !XiNa Solar One | REIPPPP_BW3 | CSP | Existing | 100 | - | - | - | - | 2049-01-01 | - | - | - | - | 0% | 3114 | 0 | - | - | - | - | 6 | 8% | 0% | -29.1621 | 19.3863
base | Adams Solar PV 2 | REIPPPP_BW3 | solar | Existing | 75 | - | - | - | - | 2043-01-01 | - | - | - | - | 0% | 2176 | 0 | - | - | - | - | - | 5% | 0% | -27.2025 | 22.8468
base | ENERGY Joburg Landfill Gas to Electircity Project | REIPPPP_BW3 | biomass | Existing | 7.56 | - | - | - | - | 2049-01-01 | - | 0 | - | - | 0% | 1109 | 0 | - | - | - | - | - | 5% | 10% | -26.195 | 28.0325
base | Karoshoek Solar One | REIPPPP_BW3 | CSP | Existing | 100 | - | - | - | - | 2049-01-01 | - | - | - | - | 0% | 3114 | 0 | - | - | - | - | 6 | 8% | 0% | -28.4149 | 21.2219
base | Khobab Wind Farm | REIPPPP_BW3 | onwind | Existing | 137.74 | - | - | - | - | 2038-01-01 | - | - | - | - | 0% | 868 | 0 | - | - | - | - | - | 6% | 0% | -30.9181 | 19.441
base | Loeriesfontein 2 Wind Farm | REIPPPP_BW3 | onwind | Existing | 138.23 | - | - | - | - | 2038-01-01 | - | - | - | - | 0% | 868 | 0 | - | - | - | - | - | 6% | 0% | -30.9181 | 19.441
base | Longyuan Mulilo De Aar Maanhaarberg Wind Energy Facility | REIPPPP_BW3 | onwind | Existing | 96.48 | - | - | - | - | 2038-01-01 | - | - | - | - | 0% | 868 | 0 | - | - | - | - | - | 6% | 0% | -30.6599 | 24.0198
base | Longyuan Mulilo Green Energy De Aar 2 North Wind Energy Facility | REIPPPP_BW3 | onwind | Existing | 138.96 | - | - | - | - | 2038-01-01 | - | - | - | - | 0% | 868 | 0 | - | - | - | - | - | 6% | 0% | -30.6599 | 24.0198
base | Mkuze | REIPPPP_BW3 | biomass | Planned | 16.5 | - | 32 | - | - | beyond 2050 | - | 1650 | - | - | 0% | 1500 | 0 | - | 6 | 4 |  |  | 0% | 0% | -27.618 | 32.0345
base | Mulilo Prieska PV | REIPPPP_BW3 | solar | Existing | 75 | - | - | - | - | 2043-01-01 | - | - | - | - | 0% | 1165 | 0 | - | - | - | - | - | 5% | 0% | -29.9647 | 22.3394
base | Mulilo Sonnedix Prieska PV | REIPPPP_BW3 | solar | Existing | 75 | - | - | - | - | 2043-01-01 | - | - | - | - | 0% | 1165 | 0 | - | - | - | - | - | 5% | 0% | -29.9647 | 22.3394
base | Nojoli Wind Farm | REIPPPP_BW3 | onwind | Existing | 86.6 | - | - | - | - | 2038-01-01 | - | - | - | - | 0% | 868 | 0 | - | - | - | - | - | 6% | 0% | -32.7461 | 25.807
base | Noupoort Wind Farm | REIPPPP_BW3 | onwind | Existing | 79.05 | - | - | - | - | 2038-01-01 | - | - | - | - | 0% | 868 | 0 | - | - | - | - | - | 6% | 0% | -31.1839 | 24.946
base | Paleisheuwel | REIPPPP_BW3 | solar | Existing | 75 | - | - | - | - | 2043-01-01 | - | - | - | - | 0% | 1165 | 0 | - | - | - | - | - | 5% | 0% | -32.1967 | 18.895
base | Pulida Solar Park | REIPPPP_BW3 | solar | Existing | 75 | - | - | - | - | 2043-01-01 | - | - | - | - | 0% | 1165 | 0 | - | - | - | - | - | 5% | 0% | -29.1333 | 24.7988
base | Red Cap - Gibson Bay | REIPPPP_BW3 | onwind | Existing | 108.25 | - | - | - | - | 2038-01-01 | - | - | - | - | 0% | 868 | 0 | - | - | - | - | - | 6% | 0% | -34.0016 | 24.7416
base | Tom Burke Solar Park | REIPPPP_BW3 | solar | Existing | 60 | - | - | - | - | 2043-01-01 | - | - | - | - | 0% | 1165 | 0 | - | - | - | - | - | 5% | 0% | -23.6719 | 27.6357
base | Kathu Solar Park | REIPPPP_BW3.5 | CSP | Existing | 100 | - | - | - | - | beyond 2050 | - | - | - | - | 0% | 2902 | 0 | - | - | - | - | 6 | 8% | 0% | -27.7581 | 23.0159
base | Redstone Solar Thermal Power Plant | REIPPPP_BW3.5 | CSP | Under construction | 100 | - | - | 2024-01-01 | - | beyond 2050 | - | - | - | - | 0% | 2902 | 0 | - | - | - | - | 9 | 8% | 0% | -28.3095 | 23.1041
base | Aggeneys Solar | REIPPPP_BW4 | solar | Existing | 40 | - | - | - | - | 2046-01-01 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | 5% | 0% | -29.2202 | 18.9152
base | Boikanyo Solar | REIPPPP_BW4 | solar | Existing | 55 | - | - | - | - | 2046-01-01 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | 5% | 0% | -29.1151 | 23.7491
base | Bokamoso | REIPPPP_BW4 | solar | Existing | 67.9 | - | - | - | - | 2046-01-01 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | 5% | 0% | -26.854 | 26.6421
base | Copperton Windfarm | REIPPPP_BW4 | onwind | Existing | 102 | - | - | - | - | 2041-01-01 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | 6% | 0% | -29.9647 | 22.3394
base | De Wildt | REIPPPP_BW4 | solar | Existing | 50 | - | - | - | - | 2046-01-01 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | 5% | 0% | -25.6097 | 27.8077
base | Dyason's Klip 1 | REIPPPP_BW4 | solar | Existing | 75 | - | - | - | - | 2046-01-01 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | 5% | 0% | -28.4149 | 21.2219
base | Dyason's Klip 2 | REIPPPP_BW4 | solar | Existing | 75 | - | - | - | - | 2046-01-01 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | 5% | 0% | -28.4149 | 21.2219
base | Excelsior Wind Energy Facility | REIPPPP_BW4 | onwind | Existing | 31.9 | - | - | - | - | 2041-01-01 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | 6% | 0% | -34.0247 | 20.4319
base | Garob Wind Farm | REIPPPP_BW4 | onwind | Existing | 135.93 | - | - | - | - | 2041-01-01 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | 6% | 0% | -29.9647 | 22.3394
base | Golden Valley Wind | REIPPPP_BW4 | onwind | Existing | 117.72 | - | - | - | - | 2041-01-01 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | 6% | 0% | -32.7461 | 25.807
base | Kangnas Wind Farm | REIPPPP_BW4 | onwind | Existing | 136.7 | - | - | - | - | 2041-01-01 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | 6% | 0% | -29.6657 | 17.8878
base | Konkoonsies II Solar PV Facility | REIPPPP_BW4 | solar | Existing | 75 | - | - | - | - | 2046-01-01 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | 5% | 0% | -29.1621 | 19.3863
base | Kruisvallei Hydro | REIPPPP_BW4 | hydro | Existing | 3.8 | - | - | - | - | beyond 2050 | - | - | - | - | 0% | 1240 | 0 | - | - | - | - | - | 3% | 3% | -28.2425 | 28.3077
base | Matla A Bokone Solar | REIPPPP_BW4 | solar | Existing | 75 | - | - | - | - | 2046-01-01 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | 5% | 0% | -28.7251 | 24.7517
base | Ngodwana Energy | REIPPPP_BW4 | biomass | Existing | 25 | - | 32 | - | - | beyond 2050 | - | 1650 | - | - | 0% | 1500 | 0 | - | 6 | 4 |  |  | 0% | 0% | -25.4809 | 30.9743
base | Nxuba Wind Farm | REIPPPP_BW4 | onwind | Existing | 138.9 | - | - | - |  | 2041-01-01 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | 6% | 0% | -32.7461 | 25.807
base | Oyster Bay Wind Farm | REIPPPP_BW4 | onwind | Existing | 140 | - | - | - |  | 2041-01-01 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | 6% | 0% | -34.0016 | 24.7416
base | Perdekraal East Wind Farm | REIPPPP_BW4 | onwind | Existing | 107.76 | - | - | - |  | 2041-01-01 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | 6% | 0% | -33.3394 | 20.0293
base | Roggeveld Wind Farm | REIPPPP_BW4 | onwind | Existing | 140 | - | - | - |  | 2041-01-01 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | 6% | 0% | -32.4095 | 20.6698
base | Sirius Solar PV Project One | REIPPPP_BW4 | solar | Existing | 75 | - | - | - |  | 2046-01-01 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | 5% | 0% | -28.4149 | 21.2219
base | Soetwater Wind Farm | REIPPPP_BW4 | onwind | Under construction | 139.4 | - | - | 2024-01-01 |  | 2042-01-01 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | 6% | 0% | -32.4095 | 20.6698
base | Solar Capital Orange | REIPPPP_BW4 | solar | Under construction | 75 | - | - | 2023-01-01 |  | 2047-01-01 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | 5% | 0% | -30.9181 | 19.441
base | The Karusa Wind Farm | REIPPPP_BW4 | onwind | Existing | 139.8 | - | - | - |  | 2046-01-01 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | 6% | 0% | -32.4095 | 20.6698
base | Waterloo Solar Park | REIPPPP_BW4 | solar | Existing | 75 | - | - | - |  | 2046-01-01 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | 5% | 0% | -26.9382 | 24.7049
base | Wesley-Ciskei | REIPPPP_BW4 | onwind | Existing | 32.7 | - | - | - |  | 2041-01-01 | - | - | - | - | 0% | 687 | 0 | - | - | - | - | - | 6% | 0% | -33.2824 | 27.4298
base | Zeerust | REIPPPP_BW4 | solar | Existing | 75 | - | - | - |  | 2046-01-01 | - | - | - | - | 0% | 872 | 0 | - | - | - | - | - | 5% | 0% | -25.2366 | 26.0824
base | Municipal_Coal | other | coal | Existing | 160 | - | - | - |  | beyond 2050 | 12.372 | 13.7 | 0.5 | 0.5 | 30% | 80 | 0 | - | - | - | - | - | 10% | 15% | -26.658 | 28.1138
base | Sasol_SSF | other | coal | Existing | 600 | - | - | - |  | beyond 2050 | 12.372 | 13.7 | 0.5 | 0.5 | 30% | 900 | 0 | - | - | - | - | - | 10% | 10% | -26.5036 | 29.1803
base | Avon | other | diesel | Existing | 670 | 167.5 | 4 | - |  | beyond 2050 | 11.519 | 250 | 11 | 11 | 0% | 2 | 101 | - | - | - | - | - | 6.9% | 4.6% | -29.251 | 31.0941
base | Dedisa | other | diesel | Existing | 335 | 167.5 | 2 | - |  | beyond 2050 | 11.519 | 250 | 11 | 11 | 0% | 2 | 101 | - | - | - | - | - | 6.9% | 4.6% | -33.4433 | 25.4022
base | Sasol_Infrach_Engines | other | gas | Existing | 175 | 9.7 | 18 | - |  | beyond 2050 | 7.6 | 200 | 8 | 8 | 0% | 950 | 0 | - | - | - | - | - | 6.9% | 4.6% | -26.8102 | 27.8277
base | Sasol_OCGT | other | gas | Existing | 250 | 50 | 5 | - |  | beyond 2050 | 11.519 | 200 | 2 | 2 | 0% | 950 | 0 | - | - | - | - | - | 6.9% | 4.6% | -26.8102 | 27.8277
base | CahoraBassa | other | hydro | Existing | 1764 | 250 | 6 | - |  | beyond 2050 | - | - | - | - | 0% | 300 | 0 | - | - | - | - | - | 3% | 3%
base | ColleyWobbles | other | hydro | Existing | 65 | 65 | 1 | - |  | beyond 2050 | - | - | - | - | 0% | 300 | 0 | - | - | - | - | - | 5% | 5% | -32.05 | 28.5833
base | Mondi | other | biomass | Existing | 120 | 30 | 4 | - |  | beyond 2050 | - | - | 0.5 | 0.5 | 0% | 500 | 0 | - | - | - | - | - | 10% | 10%
base | Sappi | other | biomass | Existing | 144 | 36 | 4 | - |  | beyond 2050 | - | - | 0.5 | 0.5 | 0% | 500 | 0 | - | - | - | - | - | 10% | 10% | -25.3447 | 30.394
base | Steenbras | other | PHS | Existing | 180 | 45 | 4 | - |  | beyond 2050 | - | - | - | - | 0% | 300 | 0 | 72% | 4 | 45 | 2.7 | - | 3% | 2.4% | -34.153 | 18.9
Formulas:
Decommissioning Date (100%) = [Decommissioning Date (100%), row above]

## new_build
scenario | parameter | carrier (MW) | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
base | max_installed_limit | solar | 2022: 0; 2023: 0; 2024: 0
base | max_installed_limit | onwind | 2022: 0; 2023: 0; 2024: 0
base | max_installed_limit | CCGT | 2022: 0; 2023: 0; 2024: 0
base | max_installed_limit | OCGT | 2022: 0; 2023: 0; 2024: 0
base | max_installed_limit | biomass | 2022: 0; 2023: 0; 2024: 0
base | max_installed_limit | coal | 2022: 0; 2023: 0; 2024: 0
base | max_installed_limit | nuclear | 2022: 0; 2023: 0; 2024: 0
base | max_installed_limit | PHS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | max_installed_limit | battery | 2022: 0; 2023: 0; 2024: 0
base | min_installed_limit | solar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | onwind | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | CCGT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | OCGT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | PHS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | min_installed_limit | battery | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## projected_parameters
scenario | parameter | unit | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050
base | annual_demand | TWh/yr | 248.3693 | 252.3981 | 256.7626 | 261.1271 | 264.3416 | 268.6277 | 272.9137 | 276.1282 | 279.8785 | 284.7003 | 287.3791 | 291.6651 | 294.8797 | 299.1657 | 302.3803 | 306.1305 | 309.8808 | 313.0954 | 316.3099 | 320.0602 | 323.2747 | 327.5607 | 330.2395 | 333.9898 | 337.7401 | 341.4904 | 344.7049 | 348.4552 | 351.6697 | 355.42
base | coal_fleet_EAF | %/yr | 0 | 0 | -0.02 | -0.02 | -0.02 | -0.01 | -0.01 | -0.01 | -0.01 | -0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
base | fast_reserves | MW | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800
base | total_reserves | MW | 2200 | 2200 | 2200 | 2200 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400 | 3400

## costs
scenario | technology | parameter | 2025 | 2030 | 2035 | 2040 | 2045 | 2050 | unit | source
original | coal | CO2 intensity |  |  |  | 0.348 |  |  | 0.348 | Original pypsa-za values for 2040 https://github.com/PyPSA/pypsa-za
original | CSP | CO2 intensity |  |  |  | 0 |  |  | tCO2/MWth
original | diesel | CO2 intensity |  |  |  | 0.248 |  |  | tCO2/MWth
original | gas | CO2 intensity |  |  |  | 0.187 |  |  | tCO2/MWth
original | solar | discount rate |  |  |  | 0.08 |  |  | per unit | Original pypsa-za values for 2040 https://github.com/PyPSA/pypsa-za
original | solar-rooftop | discount rate |  |  |  | 0.08 |  |  | per unit
original | solar-utility | discount rate |  |  |  | 0.08 |  |  | per unit
original | battery inverter | efficiency |  |  |  | 89% |  |  | per unit
original | biomass | efficiency |  |  |  | 46.8% |  |  | per unit
original | CCGT | efficiency |  |  |  | 49% |  |  | per unit | Original pypsa-za values for 2040 https://github.com/PyPSA/pypsa-za
original | coal | efficiency |  |  |  | 37% |  |  | per unit | Original pypsa-za values for 2040 https://github.com/PyPSA/pypsa-za
original | CSP | efficiency |  |  |  | 100% |  |  | per unit | Original pypsa-za values for 2040 https://github.com/PyPSA/pypsa-za
original | diesel | efficiency |  |  |  | 39.3% |  |  | per unit | Original pypsa-za values for 2040 https://github.com/PyPSA/pypsa-za
original | geothermal | efficiency |  |  |  | 23.9% |  |  | per unit
original | hydro | efficiency |  |  |  | 90% |  |  | per unit
original | nuclear | efficiency |  |  |  | 33.7% |  |  | per unit
original | OCGT | efficiency |  |  |  | 31% |  |  | per unit
original | PHS | efficiency |  |  |  | 75% |  |  | per unit
original | ror | efficiency |  |  |  | 90% |  |  | per unit
original | battery inverter | FOM |  |  |  | 2.5 |  |  | %/year
original | biomass | FOM |  |  |  | 2.6 |  |  | %/year
original | CCGT | FOM |  |  |  | 1.8 |  |  | %/year
original | coal | FOM |  |  |  | 2.6 |  |  | %/year
original | CSP | FOM |  |  |  | 5 |  |  | %/year
original | diesel | FOM |  |  |  | 2.6 |  |  | %/year
original | HVAC overhead | FOM |  |  |  | 2 |  |  | %/year
original | HVDC inverter pair | FOM |  |  |  | 2 |  |  | %/year
original | HVDC overhead | FOM |  |  |  | 2 |  |  | %/year
original | HVDC submarine | FOM |  |  |  | 2 |  |  | %/year
original | hydro | FOM |  |  |  | 1 |  |  | %/year
original | nuclear | FOM |  |  |  | 1.6 |  |  | %/year
original | OCGT | FOM |  |  |  | 2 |  |  | %/year
original | onwind | FOM |  |  |  | 4 |  |  | %/year
original | PHS | FOM |  |  |  | 1 |  |  | %/year
original | ror | FOM |  |  |  | 2 |  |  | %/year
original | solar | FOM |  |  |  | 2 |  |  | %/year
original | solar-rooftop | FOM |  |  |  | 2 |  |  | %/year
original | solar-utility | FOM |  |  |  | 2 |  |  | %/year
original | biomass | fuel | [6 empty] | ZAR/MWhth
original | coal | fuel |  |  |  | 98 |  |  | ZAR/MWhth
original | CSP | fuel |  |  |  | 50 |  |  | ZAR/MWhth
original | diesel | fuel |  |  |  | 900 |  |  | ZAR/MWhth
original | gas | fuel |  |  |  | 540 |  |  | ZAR/MWhth
original | nuclear | fuel |  |  |  | 29 |  |  | ZAR/MWhth
original | uranium | fuel |  |  |  | 0 |  |  | ZAR/MWhth
original | battery inverter | investment |  |  |  | 12000 |  |  | ZAR/kWel
original | battery storage | investment |  |  |  | 0 |  |  | ZAR/kWh
original | biomass | investment |  |  |  | 1610.361 |  |  | ZAR/kWel
original | CCGT | investment |  |  |  | 12199 |  |  | ZAR/kWel
original | coal | investment |  |  |  | 48188 |  |  | ZAR/kWel
original | CSP | investment |  |  |  | 0 |  |  | ZAR/kWel
original | diesel | investment |  |  |  | 291.6 |  |  | ZAR/kWel
original | HVAC overhead | investment |  |  |  | 6000 |  |  | ZAR/MW/km
original | HVDC inverter pair | investment |  |  |  | 0 |  |  | ZAR/MW
original | HVDC overhead | investment |  |  |  | 6000 |  |  | ZAR/MW/km
original | HVDC submarine | investment |  |  |  | 0 |  |  | ZAR/MW/km
original | hydro | investment |  |  |  | 2000 |  |  | ZAR/kWel
original | nuclear | investment |  |  |  | 91968 |  |  | ZAR/kWel
original | OCGT | investment |  |  |  | 10754 |  |  | ZAR/kWel
original | onwind | investment |  |  |  | 10544 |  |  | ZAR/kWel
original | PHS | investment |  |  |  | 2000 |  |  | ZAR/kWel
original | ror | investment |  |  |  | 3000 |  |  | ZAR/kWel
original | solar | investment |  |  |  | 5363 |  |  | ZAR/kWel
original | solar-rooftop | investment |  |  |  | 10177.2045 |  |  | ZAR/kWel
original | solar-utility | investment |  |  |  | 5363 |  |  | ZAR/kWel
original | battery inverter | lifetime |  |  |  | 20 |  |  | years
original | battery storage | lifetime |  |  |  | 20 |  |  | years
original | biomass | lifetime | [6 empty] | years
original | CCGT | lifetime |  |  |  | 30 |  |  | years
original | coal | lifetime |  |  |  | 30 |  |  | years
original | CSP | lifetime |  |  |  | 30 |  |  | years
original | diesel | lifetime | [6 empty] | years
original | HVAC overhead | lifetime |  |  |  | 40 |  |  | years
original | HVDC inverter pair | lifetime |  |  |  | 40 |  |  | years
original | HVDC overhead | lifetime |  |  |  | 40 |  |  | years
original | HVDC submarine | lifetime |  |  |  | 40 |  |  | years
original | hydro | lifetime |  |  |  | 80 |  |  | years
original | nuclear | lifetime |  |  |  | 60 |  |  | years
original | OCGT | lifetime |  |  |  | 30 |  |  | years
original | onwind | lifetime |  |  |  | 20 |  |  | years
original | PHS | lifetime |  |  |  | 80 |  |  | years
original | ror | lifetime |  |  |  | 80 |  |  | years
original | solar | lifetime |  |  |  | 25 |  |  | years
original | solar-rooftop | lifetime |  |  |  | 25 |  |  | years
original | solar-utility | lifetime |  |  |  | 25 |  |  | years
original | CCGT | VOM |  |  |  | 22 |  |  | ZAR/MWhel
original | coal | VOM |  |  |  | 80 |  |  | ZAR/MWhel
original | CSP | VOM |  |  |  | 0 |  |  | ZAR/MWhel
original | diesel | VOM |  |  |  | 3 |  |  | EUR/MWhel
original | nuclear | VOM |  |  |  | 37 |  |  | ZAR/MWhel
original | OCGT | VOM |  |  |  | 2.4 |  |  | ZAR/MWhel
original | onwind | VOM |  |  |  | 0.02 |  |  | ZAR/MWhel
original | solar | VOM |  |  |  | 0.01 |  |  | ZAR/MWhel
original | nuclear | ramp_rate |  |  |  | 100% |  |  | %/h
original | coal | ramp_rate |  |  |  | 100% |  |  | %/h
csir_2019 | coal | CO2 intensity | 0.354 | 0.354 | 0.354 | 0.354 | 0.354 | 0.354 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
csir_2019 | CSP | CO2 intensity | 0 | 0 | 0 | 0 | 0 | 0 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
csir_2019 | diesel | CO2 intensity | 0.248 | 0.248 | 0.248 | 0.248 | 0.248 | 0.248 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
csir_2019 | gas | CO2 intensity | 0.187 | 0.187 | 0.187 | 0.187 | 0.187 | 0.187 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
csir_2019 | solar | discount rate | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | per unit
csir_2019 | solar-rooftop | discount rate | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | per unit | standard for decentral
csir_2019 | solar-utility | discount rate | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | per unit | standard for decentral
csir_2019 | battery inverter | efficiency | 89% | 89% | 89% | 89% | 89% | 89% | per unit | budischak2013; Lund and Kempton (2008) http://dx.doi.org/10.1016/j.enpol.2008.06.007
csir_2019 | biomass | efficiency | 46.8% | 46.8% | 46.8% | 46.8% | 46.8% | 46.8% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | CCGT | efficiency | 49% | 49% | 49% | 49% | 49% | 49% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | coal | efficiency | 37% | 37% | 37% | 37% | 37% | 37% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348 PC (Advanced/SuperC)
csir_2019 | CSP | efficiency | 100% | 100% | 100% | 100% | 100% | 100% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348 CT
csir_2019 | diesel | efficiency | 39.3% | 39.3% | 39.3% | 39.3% | 39.3% | 39.3% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348 CT
csir_2019 | geothermal | efficiency | 23.9% | 23.9% | 23.9% | 23.9% | 23.9% | 23.9% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | hydro | efficiency | 90% | 90% | 90% | 90% | 90% | 90% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | nuclear | efficiency | 33.7% | 33.7% | 33.7% | 33.7% | 33.7% | 33.7% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | OCGT | efficiency | 31% | 31% | 31% | 31% | 31% | 31% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | PHS | efficiency | 75% | 75% | 75% | 75% | 75% | 75% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | ror | efficiency | 90% | 90% | 90% | 90% | 90% | 90% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | battery inverter | FOM | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | %/year | budischak2013
csir_2019 | biomass | FOM | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | CCGT | FOM | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | coal | FOM | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348 PC (Advanced/SuperC)
csir_2019 | CSP | FOM | 5 | 5 | 5 | 5 | 5 | 5 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | diesel | FOM | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | HVAC overhead | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | Hagspiel
csir_2019 | HVDC inverter pair | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | Hagspiel
csir_2019 | HVDC overhead | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | Hagspiel
csir_2019 | HVDC submarine | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | Hagspiel
csir_2019 | hydro | FOM | 1 | 1 | 1 | 1 | 1 | 1 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | nuclear | FOM | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | %/year
csir_2019 | OCGT | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | onwind | FOM | 4 | 4 | 4 | 4 | 4 | 4 | %/year | DEA https://ens.dk/en/our-services/projections-and-models/technology-data
csir_2019 | PHS | FOM | 1 | 1 | 1 | 1 | 1 | 1 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | ror | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | solar | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | solar-rooftop | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | ETIP PV
csir_2019 | solar-utility | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | ETIP PV
csir_2019 | biomass | fuel | [6 empty] | ZAR/MWhth | IEA2011b
csir_2019 | coal | fuel | 98 | 98 | 98 | 98 | 98 | 98 | ZAR/MWhth | IEA2011b
csir_2019 | CSP | fuel | 50 | 50 | 50 | 50 | 50 | 50 | ZAR/MWhth | IEA WEM2017 97USD/boe = http://www.iea.org/media/weowebsite/2017/WEM_Documentation_WEO2017.pdf
csir_2019 | diesel | fuel | 900 | 900 | 900 | 900 | 900 | 900 | ZAR/MWhth | IEA WEM2017 97USD/boe = http://www.iea.org/media/weowebsite/2017/WEM_Documentation_WEO2017.pdf
csir_2019 | gas | fuel | 540 | 540 | 540 | 540 | 540 | 540 | ZAR/MWhth | IEA2011b
csir_2019 | nuclear | fuel | 29 | 29 | 29 | 29 | 29 | 29 | ZAR/MWhth | IEA2011b
csir_2019 | uranium | fuel | [6 empty] | ZAR/MWhth | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | battery inverter | investment | 7872.7456 | 6593.5064 | 6181.4123 | 5769.3181 | 5357.224 | 4945.1298 | ZAR/kWel
csir_2019 | battery storage | investment | 0 | 0 | 0 | 0 | 0 | 0 | ZAR/kWh
csir_2019 | biomass | investment | 20232.7311 | 20232.7311 | 20232.7311 | 20232.7311 | 20232.7311 | 20232.7311 | ZAR/kWel
csir_2019 | CCGT | investment | 12199 | 12199 | 12199 | 12199 | 12199 | 12199 | ZAR/kWel
csir_2019 | coal | investment | 48188 | 48188 | 48188 | 48188 | 48188 | 48188 | ZAR/kWel
csir_2019 | CSP | investment | [6 empty] | ZAR/kWel
csir_2019 | diesel | investment | 400 | 360 | 324 | 291.6 | 262.44 | 236.196 | ZAR/kWel
csir_2019 | HVAC overhead | investment | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | ZAR/MW/km
csir_2019 | HVDC inverter pair | investment | [6 empty] | ZAR/MW
csir_2019 | HVDC overhead | investment | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | ZAR/MW/km
csir_2019 | HVDC submarine | investment | [6 empty] | ZAR/MW/km
csir_2019 | hydro | investment | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | ZAR/kWel
csir_2019 | nuclear | investment | 94326.6564 | 94326.6564 | 94326.6564 | 94326.6564 | 94326.6564 | 94326.6564 | ZAR/kWel
csir_2019 | OCGT | investment | 10754 | 10754 | 10754 | 10754 | 10754 | 10754 | ZAR/kWel
csir_2019 | onwind | investment | 13131 | 11831 | 11190 | 10544 | 9893 | 9238 | ZAR/kWel
csir_2019 | PHS | investment | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | ZAR/kWel
csir_2019 | ror | investment | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | ZAR/kWel
csir_2019 | solar | investment | 6671 | 5136 | 4402 | 3844 | 3506 | 3238 | ZAR/kWel
csir_2019 | solar-rooftop | investment | 6671 | 5136 | 4402 | 3844 | 3506 | 3238 | ZAR/kWel
csir_2019 | solar-utility | investment | 6671 | 5136 | 4402 | 3844 | 3506 | 3238 | ZAR/kWel
csir_2019 | battery inverter | lifetime | 20 | 20 | 20 | 20 | 20 | 20 | years | budischak2013
csir_2019 | battery storage | lifetime | 20 | 20 | 20 | 20 | 20 | 20 | years | budischak2013
csir_2019 | biomass | lifetime | [6 empty] | years | ECF2010 in DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | CCGT | lifetime | 30 | 30 | 30 | 30 | 30 | 30 | years | IEA2010
csir_2019 | coal | lifetime | 30 | 30 | 30 | 30 | 30 | 30 | years | IEA2010
csir_2019 | CSP | lifetime | 30 | 30 | 30 | 30 | 30 | 30 | years | ECF2010 in DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | diesel | lifetime | [6 empty] | years | ECF2010 in DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | HVAC overhead | lifetime | 40 | 40 | 40 | 40 | 40 | 40 | years | Hagspiel
csir_2019 | HVDC inverter pair | lifetime | 40 | 40 | 40 | 40 | 40 | 40 | years | Hagspiel
csir_2019 | HVDC overhead | lifetime | 40 | 40 | 40 | 40 | 40 | 40 | years | Hagspiel
csir_2019 | HVDC submarine | lifetime | 40 | 40 | 40 | 40 | 40 | 40 | years | Hagspiel
csir_2019 | hydro | lifetime | 80 | 80 | 80 | 80 | 80 | 80 | years | IEA2010
csir_2019 | nuclear | lifetime | 60 | 60 | 60 | 60 | 60 | 60 | years | ECF2010 in DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | OCGT | lifetime | 30 | 30 | 30 | 30 | 30 | 30 | years | IEA2010
csir_2019 | onwind | lifetime | 20 | 20 | 20 | 20 | 20 | 20 | years | DEA https://ens.dk/en/our-services/projections-and-models/technology-data
csir_2019 | PHS | lifetime | 80 | 80 | 80 | 80 | 80 | 80 | years | IEA2010
csir_2019 | ror | lifetime | 80 | 80 | 80 | 80 | 80 | 80 | years | IEA2010
csir_2019 | solar | lifetime | 25 | 25 | 25 | 25 | 25 | 25 | years | IEA2010
csir_2019 | solar-rooftop | lifetime | 25 | 25 | 25 | 25 | 25 | 25 | years | IEA2010
csir_2019 | solar-utility | lifetime | 25 | 25 | 25 | 25 | 25 | 25 | years | IEA2010
csir_2019 | CCGT | VOM | 22 | 22 | 22 | 22 | 22 | 22 | ZAR/MWhel | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | coal | VOM | 80 | 80 | 80 | 80 | 80 | 80 | ZAR/MWhel | DIW DataDoc http://hdl.handle.net/10419/80348 PC (Advanced/SuperC)
csir_2019 | CSP | VOM | 0 | 0 | 0 | 0 | 0 | 0 | ZAR/MWhel | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | diesel | VOM | 3 | 3 | 3 | 3 | 3 | 3 | EUR/MWhel | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | nuclear | VOM | 37 | 37 | 37 | 37 | 37 | 37 | ZAR/MWhel | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | OCGT | VOM | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | ZAR/MWhel | DIW DataDoc http://hdl.handle.net/10419/80348
csir_2019 | onwind | VOM | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | ZAR/MWhel | DEA https://ens.dk/en/our-services/projections-and-models/technology-data
csir_2019 | solar | VOM | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | ZAR/MWhel | RES costs made up to fix curtailment order
irp_2019 | coal | CO2 intensity | 0.354 | 0.354 | 0.354 | 0.354 | 0.354 | 0.354 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
irp_2019 | CSP | CO2 intensity | 0 | 0 | 0 | 0 | 0 | 0 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
irp_2019 | diesel | CO2 intensity | 0.248 | 0.248 | 0.248 | 0.248 | 0.248 | 0.248 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
irp_2019 | gas | CO2 intensity | 0.187 | 0.187 | 0.187 | 0.187 | 0.187 | 0.187 | tCO2/MWth | https://www.eia.gov/environment/emissions/co2_vol_mass.php
irp_2019 | solar | discount rate | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | per unit
irp_2019 | solar-rooftop | discount rate | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | per unit | standard for decentral
irp_2019 | solar-utility | discount rate | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | 0.08 | per unit | standard for decentral
irp_2019 | battery inverter | efficiency | 89% | 89% | 89% | 89% | 89% | 89% | per unit | budischak2013; Lund and Kempton (2008) http://dx.doi.org/10.1016/j.enpol.2008.06.007
irp_2019 | biomass | efficiency | 46.8% | 46.8% | 46.8% | 46.8% | 46.8% | 46.8% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | CCGT | efficiency | 49% | 49% | 49% | 49% | 49% | 49% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | coal | efficiency | 37% | 37% | 37% | 37% | 37% | 37% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348 PC (Advanced/SuperC)
irp_2019 | CSP | efficiency | 100% | 100% | 100% | 100% | 100% | 100% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348 CT
irp_2019 | diesel | efficiency | 39.3% | 39.3% | 39.3% | 39.3% | 39.3% | 39.3% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348 CT
irp_2019 | geothermal | efficiency | 23.9% | 23.9% | 23.9% | 23.9% | 23.9% | 23.9% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | hydro | efficiency | 90% | 90% | 90% | 90% | 90% | 90% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | nuclear | efficiency | 33.7% | 33.7% | 33.7% | 33.7% | 33.7% | 33.7% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | OCGT | efficiency | 31% | 31% | 31% | 31% | 31% | 31% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | PHS | efficiency | 75% | 75% | 75% | 75% | 75% | 75% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | ror | efficiency | 90% | 90% | 90% | 90% | 90% | 90% | per unit | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | battery inverter | FOM | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | %/year | budischak2013
irp_2019 | biomass | FOM | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | CCGT | FOM | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | coal | FOM | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348 PC (Advanced/SuperC)
irp_2019 | CSP | FOM | 5 | 5 | 5 | 5 | 5 | 5 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | diesel | FOM | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | HVAC overhead | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | Hagspiel
irp_2019 | HVDC inverter pair | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | Hagspiel
irp_2019 | HVDC overhead | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | Hagspiel
irp_2019 | HVDC submarine | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | Hagspiel
irp_2019 | hydro | FOM | 1 | 1 | 1 | 1 | 1 | 1 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | nuclear | FOM | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | %/year
irp_2019 | OCGT | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | onwind | FOM | 4 | 4 | 4 | 4 | 4 | 4 | %/year | DEA https://ens.dk/en/our-services/projections-and-models/technology-data
irp_2019 | PHS | FOM | 1 | 1 | 1 | 1 | 1 | 1 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | ror | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | solar | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | solar-rooftop | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | ETIP PV
irp_2019 | solar-utility | FOM | 2 | 2 | 2 | 2 | 2 | 2 | %/year | ETIP PV
irp_2019 | biomass | fuel | [6 empty] | ZAR/MWhth | IEA2011b
irp_2019 | coal | fuel | 98 | 98 | 98 | 98 | 98 | 98 | ZAR/MWhth | IEA2011b
irp_2019 | CSP | fuel | 50 | 50 | 50 | 50 | 50 | 50 | ZAR/MWhth | IEA WEM2017 97USD/boe = http://www.iea.org/media/weowebsite/2017/WEM_Documentation_WEO2017.pdf
irp_2019 | diesel | fuel | 900 | 900 | 900 | 900 | 900 | 900 | ZAR/MWhth | IEA WEM2017 97USD/boe = http://www.iea.org/media/weowebsite/2017/WEM_Documentation_WEO2017.pdf
irp_2019 | gas | fuel | 540 | 540 | 540 | 540 | 540 | 540 | ZAR/MWhth | IEA2011b
irp_2019 | nuclear | fuel | 29 | 29 | 29 | 29 | 29 | 29 | ZAR/MWhth | IEA2011b
irp_2019 | uranium | fuel | [6 empty] | ZAR/MWhth | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | battery inverter | investment | 21359.3296 | 15346.6497 | 14144.1137 | 14144.1137 | 14144.1137 | 14144.1137 | ZAR/kWel
irp_2019 | battery storage | investment | 0 | 0 | 0 | 0 | 0 | 0 | ZAR/kWh
irp_2019 | biomass | investment | 20232.7311 | 20232.7311 | 20232.7311 | 20232.7311 | 20232.7311 | 20232.7311 | ZAR/kWel
irp_2019 | CCGT | investment | 12199 | 12199 | 12199 | 12199 | 12199 | 12199 | ZAR/kWel
irp_2019 | coal | investment | 48188 | 48188 | 48188 | 48188 | 48188 | 48188 | ZAR/kWel
irp_2019 | CSP | investment | [6 empty] | ZAR/kWel
irp_2019 | diesel | investment | 400 | 360 | 324 | 291.6 | 262.44 | 236.196 | ZAR/kWel
irp_2019 | HVAC overhead | investment | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | ZAR/MW/km
irp_2019 | HVDC inverter pair | investment | [6 empty] | ZAR/MW
irp_2019 | HVDC overhead | investment | 6000 | 6000 | 6000 | 6000 | 6000 | 6000 | ZAR/MW/km
irp_2019 | HVDC submarine | investment | [6 empty] | ZAR/MW/km
irp_2019 | hydro | investment | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | ZAR/kWel
irp_2019 | nuclear | investment | 94326.6564 | 94326.6564 | 94326.6564 | 94326.6564 | 94326.6564 | 94326.6564 | ZAR/kWel
irp_2019 | OCGT | investment | 10754 | 10754 | 10754 | 10754 | 10754 | 10754 | ZAR/kWel
irp_2019 | onwind | investment | 14144 | 13722 | 13722 | 13722 | 13722 | 13722 | ZAR/kWel
irp_2019 | PHS | investment | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | ZAR/kWel
irp_2019 | ror | investment | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | ZAR/kWel
irp_2019 | solar | investment | 10140 | 8720 | 8720 | 8720 | 8720 | 8720 | ZAR/kWel
irp_2019 | solar-rooftop | investment | 10140 | 8720 | 8720 | 8720 | 8720 | 8720 | ZAR/kWel
irp_2019 | solar-utility | investment | 10140 | 8720 | 8720 | 8720 | 8720 | 8720 | ZAR/kWel
irp_2019 | battery inverter | lifetime | 20 | 20 | 20 | 20 | 20 | 20 | years | budischak2013
irp_2019 | battery storage | lifetime | 20 | 20 | 20 | 20 | 20 | 20 | years | budischak2013
irp_2019 | biomass | lifetime | [6 empty] | years | ECF2010 in DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | CCGT | lifetime | 30 | 30 | 30 | 30 | 30 | 30 | years | IEA2010
irp_2019 | coal | lifetime | 30 | 30 | 30 | 30 | 30 | 30 | years | IEA2010
irp_2019 | CSP | lifetime | 30 | 30 | 30 | 30 | 30 | 30 | years | ECF2010 in DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | diesel | lifetime | [6 empty] | years | ECF2010 in DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | HVAC overhead | lifetime | 40 | 40 | 40 | 40 | 40 | 40 | years | Hagspiel
irp_2019 | HVDC inverter pair | lifetime | 40 | 40 | 40 | 40 | 40 | 40 | years | Hagspiel
irp_2019 | HVDC overhead | lifetime | 40 | 40 | 40 | 40 | 40 | 40 | years | Hagspiel
irp_2019 | HVDC submarine | lifetime | 40 | 40 | 40 | 40 | 40 | 40 | years | Hagspiel
irp_2019 | hydro | lifetime | 80 | 80 | 80 | 80 | 80 | 80 | years | IEA2010
irp_2019 | nuclear | lifetime | 60 | 60 | 60 | 60 | 60 | 60 | years | ECF2010 in DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | OCGT | lifetime | 30 | 30 | 30 | 30 | 30 | 30 | years | IEA2010
irp_2019 | onwind | lifetime | 20 | 20 | 20 | 20 | 20 | 20 | years | DEA https://ens.dk/en/our-services/projections-and-models/technology-data
irp_2019 | PHS | lifetime | 80 | 80 | 80 | 80 | 80 | 80 | years | IEA2010
irp_2019 | ror | lifetime | 80 | 80 | 80 | 80 | 80 | 80 | years | IEA2010
irp_2019 | solar | lifetime | 25 | 25 | 25 | 25 | 25 | 25 | years | IEA2010
irp_2019 | solar-rooftop | lifetime | 25 | 25 | 25 | 25 | 25 | 25 | years | IEA2010
irp_2019 | solar-utility | lifetime | 25 | 25 | 25 | 25 | 25 | 25 | years | IEA2010
irp_2019 | CCGT | VOM | 22 | 22 | 22 | 22 | 22 | 22 | ZAR/MWhel | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | coal | VOM | 80 | 80 | 80 | 80 | 80 | 80 | ZAR/MWhel | DIW DataDoc http://hdl.handle.net/10419/80348 PC (Advanced/SuperC)
irp_2019 | CSP | VOM | 0 | 0 | 0 | 0 | 0 | 0 | ZAR/MWhel | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | diesel | VOM | 3 | 3 | 3 | 3 | 3 | 3 | EUR/MWhel | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | nuclear | VOM | 37 | 37 | 37 | 37 | 37 | 37 | ZAR/MWhel | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | OCGT | VOM | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | ZAR/MWhel | DIW DataDoc http://hdl.handle.net/10419/80348
irp_2019 | onwind | VOM | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | ZAR/MWhel | DEA https://ens.dk/en/our-services/projections-and-models/technology-data
irp_2019 | solar | VOM | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | ZAR/MWhel | RES costs made up to fix curtailment order