## Sheet1
Power Station Name | Owner | Fuel/technology type | Status | Installed/ Operational Capacity in 2016 (MW) | Unit size (MW) | Number units | Commissioning Date | Decommissioning Date | Heat Rate (GJ/MWh) | Fuel Price (R/GJ) | Max Ramp Up (MW/min) | Variable Operations and Maintenance Cost (R/MWh) | Fixed Operations and maintenance costs (R/kW/yr) | Pump Efficiency (%) | Pump Units | Pump Load per unit (MW) | Pumped Storage - Max Storage (GWh) | CSP Storage (hours) | Typical annual maintenance rate (%) | Typical annual forced outage rate (%) | GPS Latitude | GPS Longitude
Arnot | Eskom | coal | Existing | 2220 | 370 | 6 |  | 2025-01-01 | 11.654 | 16.8 | 2.1 | 57 | 594 | - | - | - | - | - | 10 | 10 | -25.9444 | 29.7917
Camden | Eskom | coal | Existing | 1520 | 190 | 8 |  | 2023-01-01 | 12.421 | 23.1 | 1.1 | 57 | 594 | - | - | - | - | - | 10 | 10 | -26.6201 | 30.0911
Duvha | Eskom | coal | Existing | 2900 | 580 | 5 |  | 2034-01-01 | 11.034 | 11.8 | 3.3 | 57 | 594 | - | - | - | - | - | 10 | 10 | -25.9595 | 29.3409
Grootvlei | Eskom | coal | Existing | 1080 | 180 | 6 |  | 2028-01-01 | 12.61 | 22.1 | 0.9 | 57 | 594 | - | - | - | - | - | 10 | 10 | -26.7695 | 28.4995
Hendrina | Eskom | coal | Existing | 1900 | 190 | 10 |  | 2026-01-01 | 12.131 | 17 | 1.1 | 57 | 594 | - | - | - | - | - | 10 | 10 | -26.0314 | 29.6014
Kendal | Eskom | coal | Existing | 3840 | 640 | 6 |  | 2043-01-01 | 11.753 | 18.6 | 1.8 | 57 | 594 | - | - | - | - | - | 10 | 10 | -26.088 | 28.9689
Komati | Eskom | coal | Existing | 900 | 100 | 9 |  | 2028-01-01 | 13.829 | 17.6 | 0.5 | 57 | 594 | - | - | - | - | - | 10 | 10 | -26.0908 | 29.4745
Kriel | Eskom | coal | Existing | 2880 | 480 | 6 |  | 2029-01-01 | 11.243 | 18.6 | 3.6 | 57 | 594 | - | - | - | - | - | 10 | 10 | -26.254 | 29.1801
Kusile | Eskom | coal | Under construction | 0 | 723 | 0 | 2025-01-01 | beyond 2050 | 9.812 | 16.3 | 7.2 | 80 | 4700 (includes capex) | - | - | - | - | - | 10 | 10 | -25.5459 | 28.5502
Lethabo | Eskom | coal | Existing | 3540 | 590 | 6 |  | 2040-01-01 | 10.975 | 11.2 | 5.9 | 57 | 594 | - | - | - | - | - | 10 | 10 | -26.7403 | 27.975
MajubaDry | Eskom | coal | Existing | 1830 | 610 | 3 |  | 2048-01-01 | 11.753 | 21.8 | 1.7 | 57 | 594 | - | - | - | - | - | 10 | 10 | -27.0955 | 29.7706
MajubaWet | Eskom | coal | Existing | 2010 | 670 | 3 |  | 2051-01-01 | 11.004 | 23.3 | 1.9 | 57 | 594 | - | - | - | - | - | 10 | 10 | -27.0955 | 29.7706
Matimba | Eskom | coal | Existing | 3720 | 620 | 6 |  | 2041-01-01 | 11.654 | 11.4 | 3 | 57 | 594 | - | - | - | - | - | 10 | 10 | -23.6678 | 27.6128
Matla | Eskom | coal | Existing | 3480 | 580 | 6 |  | 2033-01-01 | 11.034 | 22.9 | 2.4 | 57 | 594 | - | - | - | - | - | 10 | 10 | -26.2804 | 29.1423
Medupi | Eskom | coal | Existing | 722 | 722 | 1 |  | beyond 2050 | 9.812 | 16.3 | 7.2 | 80 | 4700 (includes capex) | - | - | - | - | - | 10 | 10 | -23.42 | 27.33
Tutuka | Eskom | coal | Existing | 3480 | 580 | 6 |  | 2040-01-01 | 10.918 | 26 | 3.2 | 57 | 594 | - | - | - | - | - | 10 | 10 | -26.7756 | 29.3521
Sere | Eskom | onwind | Existing | 100 | 2 | 50 |  | 2034-04-30 | - | - | - | 700 | 0 | - | - | - | - | - | 10 | 10 | -31.5018 | 18.1143
Koeberg | Eskom | nuclear | Existing | 1860 | 930 | 2 |  | 2044-01-01 | 11.111 | 8.1 | - | 37 | 968 | - | - | - | - | - | 3 | 6 | -33.6737 | 18.4281
Drakensberg | Eskom | PHS | Existing | 1000 | 250 | 4 |  | beyond 2050 | - | - | - | 0 | 201 | 73.7 | 4 | 250 | 21.7 | - | 3 | 2.4 | -28.5628 | 29.0828
Ingula | Eskom | PHS | Existing | 1332 | 333 | 4 |  | beyond 2050 | - | - | - | 0 | 2530 (includes capex) | 78 | 4 | 333 | 27.4 | - | 3 | 2.4 | -28.165 | 29.3512
Palmiet | Eskom | PHS | Existing | 400 | 200 | 2 |  | beyond 2050 | - | - | - | 0 | 201 | 77.9 | 2 | 200 | 10 | - | 3 | 2.4 | -34.1972 | 18.9736
Gariep | Eskom | hydro | Existing | 360 | 90 | 4 |  | beyond 2050 | - | - | - | 30 | 0 | - | - | - | - | - | 3 | 2.4 | -30.624 | 25.504
Vanderkloof | Eskom | hydro | Existing | 240 | 120 | 2 |  | beyond 2050 | - | - | - | 30 | 0 | - | - | - | - | - | 3 | 2.4 | -29.9934 | 24.7338
Acacia | Eskom | oil | Existing | 171 | 57 | 3 |  | 2025-12-31 | 11.519 | 270 | 3.4 | 2 | 161 | - | - | - | - | - | 6.9 | 4.6 | -33.8841 | 18.5336
Ankerlig | Eskom | oil | Existing | 1332 | 148 | 9 |  | 2036-12-31 | 11.519 | 250 | 9 | 2 | 161 | - | - | - | - | - | 6.9 | 4.6 | -33.592 | 18.4607
Gourikwa | Eskom | oil | Existing | 740 | 148 | 5 |  | 2036-12-31 | 11.519 | 250 | 9 | 2 | 161 | - | - | - | - | - | 6.9 | 4.6 | -34.1653 | 21.9608
PortRex | Eskom | oil | Existing | 171 | 57 | 3 |  | 2025-12-31 | 11.519 | 270 | 3.4 | 2 | 161 | - | - | - | - | - | 6.9 | 4.6 | -33.0274 | 27.8838
Biomass_Round3 | Independent Power Producers | biomass | Under construction | 0 | - | - | 2026-01-01 | beyond 2050 | - | 32 | - | 1650 | 0 | - | - | - | - | - | 6 | 4
Biomass_Round4 | Independent Power Producers | biomass | Under construction | 0 | - | - | 2026-01-01 | beyond 2050 | - | 32 | - | 1610 | 0 | - | - | - | - | - | 6 | 4
Biomass_Round4_Expedited | Independent Power Producers | biomass | Committed | 0 | - | - | 2026-01-01 | beyond 2050 | - | 32 | - | 1610 | 0 | - | - | - | - | - | 6 | 4
CSP_Bokpoort_Round2_9h | Independent Power Producers | CSP | Existing | 50 | - | - |  | beyond 2050 | - | - | - | 3324 | 0 | - | - | - | - | 9 | 8 | 0 | -28.4327 | 21.5935
CSP_Karoshoek_Round3_6h | Independent Power Producers | CSP | Under construction | 0 | - | - | 2026-01-01 | beyond 2050 | - | - | - | 3114 | 0 | - | - | - | - | 6 | 8 | 0 | -27.8723 | 26.6875
CSP_Kathu Solar Park_Round3.5_6h | Independent Power Producers | CSP | Committed | 0 | - | - | 2026-01-01 | beyond 2050 | - | - | - | 2902 | 0 | - | - | - | - | 6 | 8 | 0
CSP_KaXu Solar One_Round1_3h | Independent Power Producers | CSP | Existing | 100 | - | - |  | beyond 2050 | - | - | - | 3554 | 0 | - | - | - | - | 3 | 8 | 0 | -28.5252 | 19.3535
CSP_Khi Solar One_Round1_6h | Independent Power Producers | CSP | Existing | 50 | - | - |  | beyond 2050 | - | - | - | 3554 | 0 | - | - | - | - | 6 | 8 | 0 | -28.3214 | 21.439
CSP_Redstone Solar_Round3.5_9h | Independent Power Producers | CSP | Committed | 0 | - | - | 2026-01-01 | beyond 2050 | - | - | - | 2902 | 0 | - | - | - | - | 9 | 8 | 0
CSP_Round4_9h_Expedited | Independent Power Producers | CSP | Committed | 0 | - | - | 2026-01-01 | beyond 2050 | - | - | - | 2020 | 0 | - | - | - | - | 9 | 8 | 0
CSP_XiNa Solar One_Round3_6h | Independent Power Producers | CSP | Under construction | 0 | - | - |  | beyond 2050 | - | - | - | 3114 | 0 | - | - | - | - | 6 | 8 | 0
Landfill_Gas_Round3 | Independent Power Producers | biomass | Under construction | 0 | - | - |  | beyond 2050 | - | 0 | - | 1109 | 0 | - | - | - | - | - | 5 | 10
Landfill_Gas_Round4_Expedited | Independent Power Producers | biomass | Committed | 0 | - | - | 2026-01-01 | beyond 2050 | - | 0 | - | 1109 | 0 | - | - | - | - | - | 5 | 10
Photovoltaic_Round1 | Independent Power Producers | solar | Existing | 627 | - | - |  | beyond 2050 | - | - | - | 3649 | 0 | - | - | - | - | - | 5 | 0
Photovoltaic_Round2 | Independent Power Producers | solar | Existing | 417 | - | - |  | beyond 2050 | - | - | - | 2176 | 0 | - | - | - | - | - | 5 | 0
Photovoltaic_Round3 | Independent Power Producers | solar | Existing | 435 | - | - |  | beyond 2050 | - | - | - | 1165 | 0 | - | - | - | - | - | 5 | 0
Photovoltaic_Round4 | Independent Power Producers | solar | Committed | 0 | - | - | 2026-01-01 | beyond 2050 | - | - | - | 872 | 0 | - | - | - | - | - | 5 | 0
Photovoltaic_Round4_Additional | Independent Power Producers | solar | Committed | 0 | - | - | 2026-01-01 | beyond 2050 | - | - | - | 946 | 0 | - | - | - | - | - | 5 | 0
Photovoltaic_Round4_Expedited | Independent Power Producers | solar | Committed | 0 | - | - | 2026-01-01 | beyond 2050 | - | - | - | 617 | 0 | - | - | - | - | - | 5 | 0
Small_Hydro_Round2 | Independent Power Producers | hydro | Existing | 14 | - | - |  | beyond 2050 | - | - | - | 1363 | 0 | - | - | - | - | - | 3 | 3
Small_Hydro_Round4 | Independent Power Producers | hydro | Committed | 0 | - | - | 2026-01-01 | beyond 2050 | - | - | - | 1240 | 0 | - | - | - | - | - | 3 | 3
Small_Hydro_Round4_Expedited | Independent Power Producers | hydro | Committed | 0 | - | - | 2026-01-01 | beyond 2050 | - | - | - | 1240 | 0 | - | - | - | - | - | 3 | 3
Wind_Round1 | Independent Power Producers | onwind | Existing | 634 | - | - |  | beyond 2050 | - | - | - | 1513 | 0 | - | - | - | - | - | 6 | 0
Wind_Round2 | Independent Power Producers | onwind | Existing | 564 | - | - |  | beyond 2050 | - | - | - | 1186 | 0 | - | - | - | - | - | 6 | 0
Wind_Round3 | Independent Power Producers | onwind | Under construction | 154 | - | - |  | beyond 2050 | - | - | - | 868 | 0 | - | - | - | - | - | 6 | 0
Wind_Round4 | Independent Power Producers | onwind | Committed | 0 | - | - | 2026-01-01 | beyond 2050 | - | - | - | 687 | 0 | - | - | - | - | - | 6 | 0
Wind_Round4_Additional | Independent Power Producers | onwind | Committed | 0 | - | - | 2026-01-01 | beyond 2050 | - | - | - | 801 | 0 | - | - | - | - | - | 6 | 0
Wind_Round4_Expedited | Independent Power Producers | onwind | Committed | 0 | - | - | 2026-01-01 | beyond 2050 | - | - | - | 617 | 0 | - | - | - | - | - | 6 | 0
CoalIPP_Khanyisa | Independent Power Producers | coal | Committed | 0 | 153 | - | 2026-01-01 | beyond 2050 | 10.788 | 13.7 | 3.06 | 173 | 4907 (includes capex) | - | - | - | - | - | 6 | 5
CoalIPP_Thabametsi | Independent Power Producers | coal | Committed | 0 | 140 | - | 2026-01-01 | beyond 2050 | 10.788 | 13.7 | 2.7865 | 173 | 4907 (includes capex) | - | - | - | - | - | 6 | 5
Municipal_Coal | South African Municipality | coal | Existing | 160 | - | - |  | beyond 2050 | 12.372 | 13.7 | 0.5 | 80 | 0 | - | - | - | - | - | 10 | 15 | -26.658 | 28.1138
Sasol_SSF | Sasol | coal | Existing | 600 | - | - |  | beyond 2050 | 12.372 | 13.7 | 0.5 | 900 | 0 | - | - | - | - | - | 10 | 10 | -26.5036 | 29.1803
Avon_Peaking | Independent Power Producers | oil | Existing | 670 | 167.5 | 4 |  | beyond 2050 | 11.519 | 250 | 11 | 2 | 101 | - | - | - | - | - | 6.9 | 4.6 | -29.251 | 31.0941
Dedisa_Peaking | Independent Power Producers | oil | Existing | 335 | 167.5 | 2 |  | beyond 2050 | 11.519 | 250 | 11 | 2 | 101 | - | - | - | - | - | 6.9 | 4.6 | -33.4433 | 25.4022
Sasol_Infrach_Engines | Sasol | gas | Existing | 175 | 9.7 | 18 |  | beyond 2050 | 7.6 | 200 | 8 | 950 | 0 | - | - | - | - | - | 6.9 | 4.6 | -26.8102 | 27.8277
Sasol_OCGT | Sasol | gas | Existing | 250 | 50 | 5 |  | beyond 2050 | 11.519 | 200 | 2 | 950 | 0 | - | - | - | - | - | 6.9 | 4.6 | -26.8102 | 27.8277
CahoraBassa | Import from Mozambique | hydro | Existing | 1500 | 250 | 6 |  | beyond 2050 | - | - | - | 300 | 0 | - | - | - | - | - | 3 | 3
ColleyWobbles | Eskom | hydro | Existing | 65 | 65 | 1 |  | beyond 2050 | - | - | - | 300 | 0 | - | - | - | - | - | 5 | 5 | -32.05 | 28.5833
Mondi | Independent Power Producers | biomass | Existing | 120 | 30 | 4 |  | beyond 2050 | - | - | 0.5 | 500 | 0 | - | - | - | - | - | 10 | 10
Sappi | Independent Power Producers | biomass | Existing | 144 | 36 | 4 |  | beyond 2050 | - | - | 0.5 | 500 | 0 | - | - | - | - | - | 10 | 10 | -25.3447 | 30.394
Steenbras | South African Municipality | PHS | Existing | 180 | 45 | 4 |  | beyond 2050 | - | - | - | 300 | 0 | 72 | 4 | 45 | 2.7 | - | 3 | 2.4 | -34.153 | 18.9